Hold

Sanitary Sewer Management Plan

Revised November 5, 2025

Prepared by

Environmental Health & Safety

Design, Facilities and Safety Services

Table of Contents

Tables	ii

Appendices	ii

Acronyms and Abbreviations	iii

1. Sewer System Management Plan Goal and Introduction	1

1.1. Regulatory Context	1

1.2. Sewer System Management Plan Update Schedule	1

1.3. Sewer System Asset Overview	2

2. Organization	3

2.1 Roles and Responsibilities for SSMP Implementation	4

2.2 Chain of Communication for Spill Reporting	5

3. Legal Authority	5

4. Operation and Maintenance Program	6

4.1. Updated Map of Sanitary Sewer System	7

4.2. Preventive Operation and Maintenance Activities	7

4.3. Training	10

4.4. Equipment Inventory	10

5. Design and Performance Provisions	10

5.1. Updated Design Criteria and Construction Standards and Specifications	10

5.2. Procedures and Standards	11

6. Spill Emergency Response Plan	11

7. Sewer Pipe Blockage Control Program	12

8. System Evaluation, Capacity Assurance and Capital Improvements	13

8.1 System Evaluation and Condition Assessment	13

8.2. Capacity Assessment and Design Criteria	15

8.3. Prioritization of Corrective Action	16

8.4. Capital Improvement Plan	16

9. Monitoring, Measurement and Program Modifications	17

10. Internal Audits	17

11. Communication Program	18

12. References	18

# Tables

Table 1-1 UCSB Audit Schedule

Table 1-2 UCSB Plan Update Schedule

Table 2-1 UCSB Personnel with Key Sanitary Sewer System Responsibilities

Table 2-2 UCSB Sanitary Sewer System Organization

Table 4-1 UCSB Pump and Building Lift Stations

Table 4-2 UCSB Grease Interceptors and Traps

# Appendices

Appendix A: UCSB Sanitary Sewer System Service Area Boundary

Appendix B: Goleta Beach Park Spill Emergency Response Plan

Appendix C: UCSB Spill Emergency Response Plan

# Acronyms and Abbreviations

CCTV	Closed-Circuit Television

CIWQS 	California Integrated Water Quality System Project

CMMS 	Computerized Maintenance Management Systems

DCS	Design & Construction Services

EH&S 	Environmental Health & Safety

FM	Facilities Management

General Order	Statewide Waste Discharge Requirements General Order for Sanitary Sewer Systems

(SWRCB Order No. 2022-0103-DWQ)

GIS		Geographic Information System

GPM		Gallons Per Minute

GSD		Goleta Sanitary District

GWSD		Goleta West Sanitary District

HDAE		Housing, Dining & Auxiliary Enterprises

LRO		Legally Responsible Official

Plan		Sewer System Management Plan

SERP		Spill Emergency Response Plan

SSO 		Sanitary Sewer Overflow

STI		Steel Tank Institute

SWRCB		California State Water Resources Control Board

UCPD		UC Santa Barbara Police Department

UCSB		University of California, Santa Barbara

WDID		Waste Discharge Identification

# 1. Sewer System Management Plan Goal and Introduction

Regulatory Requirement - The goal of the Sewer System Management Plan is to provide a plan and schedule to: (1) properly manage, operate, and maintain all parts of the Enrollee’s sanitary sewer system(s), (2) reduce and prevent spills, and (3) contain and mitigate spills that do occur.

The goal of this Sewer System Management Plan (Plan) is to provide a plan and schedule to:

- properly manage, operate, and maintain all parts of the sanitary sewer system;

- reduce and prevent spills; and

- contain and mitigate spills that do occur.

## 1.1. Regulatory Context

Regulatory Requirement - The Plan Introduction section must provide a general description of the local sewer system management program and discuss Plan implementation and updates.

On May 2, 2006, the California State Water Resources Control Board (SWRCB) promulgated the Statewide General Waste Discharge Requirements for Sanitary Sewer Systems (SWRCB Order No. 2006-0003) requiring, among other things, local public sewer collection system agencies, including the University of California, Santa Barbara (UCSB), to develop a Sewer System Management Plan.

On July 30, 2013, Attachment A to the Order was promulgated and became effective on September 9, 2013 (Attachment A, SWRCB Order No. WQO 2013-0058-EXEC), amending the Monitoring and Reporting Program for Statewide General Waste Discharge Requirements for Sanitary Sewer Systems.

On December 6, 2022 the SWRCB adopted the Statewide Waste Discharge Requirements General Order for Sanitary Sewer Systems (SWRCB Order No. 2022-0103-DWQ) (General Order) and became effective on June 5, 2023 (SWRCB, 2022). This General Order supersedes the previous SWRCB Order No. 2006-0003 and amendments thereafter.

## 1.2. Sewer System Management Plan Update Schedule

Regulatory Requirement - The Plan Introduction section must include a schedule for the Enrollee to update the Plan, including the schedule for conducting internal audits. The schedule must include milestones for incorporation of activities addressing prevention of sewer spills.

Plan updates are due within six (6) years after the required due date of the last Plan update. This Plan must be self-audited at least every three (3) years and a 3-Year Audit Report is due within six (6) months after the end of the last required audit period. Additionally, this Plan will be periodically reviewed and updated whenever:

- Significant work/procedures/programs/organizational changes are made; or

- A review of sanitary sewer spills and spill response efforts identifies necessary changes to improve spill response and/or prevention; or

- Plan audits are completed, and significant changes and/or deficiencies are identified.

The Legally Responsible Official (LRO) is responsible for submitting and certifying audit reports and Plan updates in the California Integrated Water Quality System Project (CIWQS) computer system. UCSB’s internal audit and Plan update schedules are shown in Tables 1-1 and 1-2, respectively.

Table 1-1

UCSB Audit Schedule

| Audit Period | Audit Report Due Date | Audit Report Certification Date |
| --- | --- | --- |
| 08/02/2021 - 08/02/2024 | 02/02/2025 | 01/31/2025 |
| 08/03/2024 - 08/02/2027 | 02/02/2028 |  |
| 08/03/2027 - 08/02/2030 | 02/02/2031 |  |

Table 1-2

UCSB Plan Update Schedule

| Plan Period | Plan Due Date | Plan Certification Date |
| --- | --- | --- |
| 08/03/2019 - 08/02/2025 | 08/02/2025 | 07/30/2025 |
| 08/03/2025 - 08/02/2031 | 08/02/2031 |  |

## 1.3. Sewer System Asset Overview

Regulatory Requirement - The Plan Introduction section must provide a description of the Enrollee-owned assets and service area, including but not limited to:

- Location, including county(ies);

- Service area boundary;

- Population and community served;

- System size, including total length in miles, length of gravity mainlines, length of pressurized (force) mains, and number of pump stations and siphons;

- Structures diverting stormwater to the sewer system;

- Data management systems;

- Sewer system ownership and operation responsibilities between Enrollee and private entities for upper and lower sewer laterals;

- Estimated number or percent of residential, commercial, and industrial service connections; and

- Unique service boundary conditions and challenge(s).

Additionally, the Plan Introduction section must provide reference to the Enrollee’s up-to-date map of its sanitary sewer system, as required in section 4.1 (Updated Map of Sanitary Sewer System) of this Attachment.

UCSB is one of 10 University of California campuses governed by the Regents of the University of California and is an internationally recognized public teaching and research institution. The campus population includes approximately 26,113 students and 12,538 faculty and staff (UCSB, 2024a).

The UCSB campus is located approximately 10 miles west of the City of Santa Barbara in an unincorporated area of Santa Barbara County. This portion of the County is referred to as the South Coast region and occupies a coastal plain about three miles wide between the Pacific Ocean and the foothills of the Santa Ynez Mountains.

The UCSB campus encompasses approximately 1,055 acres and is comprised of four areas known as the Main Campus, Storke Campus, West Campus, and North Campus.

- The Main Campus (422 acres) contains most of the UCSB academic and support buildings and facilities. Student dormitories are also located on the Main Campus, primarily in the southwest and southeast portions of the Campus. The Main Campus is located east of and adjacent to the unincorporated residential community of Isla Vista.

- The Storke Campus (184 acres) has been used for the development of student housing, parking facilities, athletic fields, and contains natural areas including the Storke Wetlands. The Storke Campus is located north of and adjacent to the Isla Vista community.

- The West Campus (273 acres) is largely devoted to a UCSB natural reserve that includes the Devereux Slough and Coal Oil Point Reserve. The West Campus also includes the former Devereux School property, and student family and faculty housing,

- The North Campus (174 acres) borders the City of Goleta and includes permanent open space area, faculty housing, and student housing.

The sanitary sewer service area intersects all four campuses, as shown in Appendix A. Wastewater from the Main Campus and a portion of the Storke Campus is conveyed through a pump station near Henley Gate and discharges to the Goleta Sanitary District (GSD) for treatment (WDID: 3 420102001). The remaining area of the Storke Campus along with the West Campus and North Campus, discharge to the Goleta West Sanitary District (GWSD) (WDID: 3SSO11465).

Additionally, sewage from facilities at Goleta Beach Park discharge into the UCSB sanitary sewer system. Accordingly, UCSB requires Goleta Beach Park to submit a Spill Emergency Response Plan (SERP), included in Appendix B. Facilities at the Goleta Beach Park consist of public restrooms, park ranger residences and offices, and a restaurant. Sanitary sewer system infrastructure at the park includes a grease interceptor and lift station. UCSB is not responsible for the operation, inspection, maintenance, or capital improvement of the sanitary sewer system infrastructure at the Goleta Beach Park.

The UCSB sanitary sewer system consists of approximately 6.82 miles of gravity main lines and 2.76 miles of pressurized (force) mains, with pipe diameters ranging from 4 to 18 inches. Pipe materials include vitrified clay (VCP), cast iron (CI), polyvinyl chloride (PVC), and asbestos cement (AC). System connections are approximately 20.4% residential and 79.6% commercial.

Key system assets include four (4) main pump stations and seventeen (17) building lift stations as well as eight (8) grease interceptors and three (3) grease traps.

# 2. Organization

Regulatory Requirement - The Plan must identify organizational staffing responsible and integral for implementing the local Sewer System Management Plan through an organization chart or similar narrative documentation that includes:

- The name of the Legally Responsible Official as required in section 5.1 (Designation of a Legally Responsible Official) of this General Order;

- The position titles, telephone numbers, and email addresses for management, administrative, and maintenance positions responsible for implementing specific Sewer System Management Plan elements;

- Organizational lines of authority; and

- Chain of communication for reporting spills from receipt of complaint or other information, including the person responsible for reporting spills to the State and Regional Water Boards and other agencies, as applicable. (For example, county health officer, county environmental health agency, and State Office of Emergency Services.)

## 2.1 Roles and Responsibilities for SSMP Implementation

The administrative responsibility for the UCSB sanitary sewer system is shared between several departments including Environmental Health & Safety (EH&S); Facilities Management (FM); Design & Construction Services (DCS); and Housing, Dining & Auxiliary Enterprises (HDAE). The responsibilities and contact information for key individuals in each department are summarized in Table 2-1. An organizational chart is shown in Table 2-2.

Table 2-1

UCSB Personnel with Key Sanitary Sewer System Responsibilities

| Name, Title | Contact Information | Responsibility |
| --- | --- | --- |
| Ali Aghayan (LRO) Environmental Health Program Manager | ali.aghayan@ucsb.edu, (805) 893-8533 | Plan development, implementation, audits, and reporting to regulatory agencies |
| Tom Polansky (LRO) Associate Director, Building Maintenance | polansky@ucsb.edu, (805) 364-7122 | Overall performance and operation of the sanitary sewer system, including making major capital improvement recommendations |
| Mason King (Data Submitter) Environmental Compliance Manager | masonking@ucsb.edu (805) 893-8997 | Plan development, implementation, audits, and reporting to regulatory agencies |
| Allison Andrade (Data Submitter) Environmental Compliance Specialist | allisonandrade@ucsb.edu (805) 893-5252 | Plan development, implementation, audits, and reporting to regulatory agencies |
| Mark Irwin Sr. Superintendent, Plumbing Services | mark.irwin@ucsb.edu (805) 722-8397 | Overall performance and operation of the sanitary sewer system, including making major capital improvement recommendations |
| Waylon Nunez Underground Utility Operator | wnunez@ucsb.edu (805) 893-8300 | Operation, inspection and maintenance of pipelines and manholes |
| Mike Smiyun Sr. Superintendent, HVAC Services | mikhail.smiyun@ucsb.edu (805) 451-8990 | Operation, inspection and maintenance of pump and building lift stations |
| Mike Lindner Sr. Superintendent, Preventative Maintenance | michael.lindner@ucsb.edu (805) 319-6624 | Operation, inspection and maintenance of pump and building lift stations and emergency standby generators |
| Steve Federlein Sr. Superintendent, Physical Plant | sfederlein@housing.ucsb.edu (805) 893-3312 | Maintenance of grease traps and interceptors |
| Paul Bartsch GIS Programmer | paul.bartsch@ucsb.edu (805) 451-7309 | Maintains up-to-date maps of the sanitary sewer and stormwater conveyance system infrastructure |

Table 2-2

UCSB Sanitary Sewer System Organization

| Element Number | Element Title | Responsible Person |
| --- | --- | --- |
| 1 | Goal and Introduction | Ali Aghayan |
| 2 | Organization | Ali Aghayan |
| 3 | Legal Authority | Ali Aghayan |
| 4 | Operation and Maintenance Program | Ali Aghayan |
| 5 | Design and Performance Provisions | Ali Aghayan |
| 6 | Spill Emergency Response Plan | Ali Aghayan |
| 7 | Sewer Pipe Blockage Control Program | Ali Aghayan |
| 8 | System Evaluation, Capacity Assurance, and Capital Improvements | Ali Aghayan |
| 9 | Monitoring, Measurement and Program Modifications | Ali Aghayan |
| 10 | Internal Audits | Ali Aghayan |
| 11 | Communication Program | Ali Aghayan |

## 2.2 Chain of Communication for Spill Reporting

In the event of a sanitary sewer spill, the employee who first identifies the spill will immediately notify:

- Facilities Management Customer Service Line (805-893-8300); or

- Housing, Dining & Auxiliary Enterprises Customer Service Line (805-893-3312); and

- Environmental Health & Safety (805-893-7534).

If a sanitary sewer spill is identified outside of normal business hours, the employee will immediately notify UCSB Police Department (UCPD) Non-Emergency (805-893-3446). UCPD will notify the on-call person responsible for spill emergency response.

The responding or on-call person will contact the Environmental Health Program Manager (LRO), Environmental Compliance Manager (Data Submitter), or Environmental Compliance Specialist (Data Submitter) to make the initial notification to Cal OES within 2 hours of knowledge of a spill of 1,000 gallons or more, discharging or threatening to discharge to surface waters. LROs and Data Submitters will review spill response efforts and spill volume calculations and prepare any revised reports to Cal OES and CIWQS. The LRO will review and certify all reports submitted through CIWQS.

Additional spill reporting procedures are described in further detail in UCSB’s SERP.

# 3. Legal Authority

Regulatory Requirement - The Plan must include copies or an electronic link to the Enrollee’s current sewer system use ordinances, service agreements and/or other legally binding procedures to demonstrate the Enrollee possesses the necessary legal authority to:

- Prevent illicit discharges into its sanitary sewer system from inflow and infiltration (I&I); unauthorized stormwater; chemical dumping; unauthorized debris; roots; fats, oils, and grease; and trash, including rags and other debris that may cause blockages;

- Collaborate with storm sewer agencies to coordinate emergency spill responses, ensure access to storm sewer systems during spill events, and prevent unintentional cross connections of sanitary sewer infrastructure to storm sewer infrastructure;

- Require that sewer system components and connections be properly designed and constructed;

- Ensure access for maintenance, inspection, and/or repairs for portions of the service lateral owned and/or operated by the Enrollee;

- Enforce any violation of its sewer ordinances, service agreements, or other legally binding procedures; and

- Obtain easement accessibility agreements for locations requiring sewer system operations and maintenance, as applicable.

The Regents of the University of California is a Constitutional Corporation, organized under Article IX, Section 9 of the California Constitution, with full authority over governance and management of the University operations. Under this authority, the University of California has legal authority to:

- Prevent illicit discharges into its sanitary sewer system from inflow and infiltration (I&I); unauthorized stormwater; chemical dumping; unauthorized debris; roots; fats, oils, and grease; and trash, including rags and other debris that may cause blockages;

- Collaborate with storm sewer agencies to coordinate emergency spill responses, ensure access to storm sewer systems during spill events, and prevent unintentional cross connections of sanitary sewer infrastructure to storm sewer infrastructure;

- Require that sewer system components and connections be properly designed and constructed;

- Ensure access for maintenance, inspection, and/or repairs for portions of the service lateral owned and/or operated by the Enrollee;

- Enforce any violation of its sewer ordinances, service agreements, or other legally binding procedures; and

- Obtain easement accessibility agreements for locations requiring sewer system operations and maintenance, as applicable.

# 4. Operation and Maintenance Program

Regulatory Requirement - The Plan must include the items listed below that are appropriate and applicable to the Enrollee’s system. An up-to-date map(s) of the sanitary sewer system, and procedures for maintaining and providing State and Regional Water Board staff access to the map(s). The map(s) must show gravity line segments and manholes, pumping facilities, pressure pipes and valves, and applicable stormwater conveyance facilities within the sewer system service area boundaries.

This section includes procedures for maintaining and updating system maps, conducting preventive operation and maintenance activities, providing regular staff training, and maintaining an equipment inventory. UCSB ensures that up-to-date Geographic Information System (GIS) maps are available and accessible to State and Regional Water Board staff, depicting all relevant infrastructure such as gravity mains, manholes, pump stations, pressure pipes, and associated stormwater conveyance features within the sewer system service area.

## 4.1. Updated Map of Sanitary Sewer System

Regulatory Requirements - The map(s) must show gravity line segments and manholes, pumping facilities, pressure pipes and valves, and applicable stormwater conveyance facilities within the sewer system service area boundaries.

Availability of up-to-date sewer system maps that include:

- All current infrastructure assets owned and operated by the agency (gravity mains, manholes, pump stations, pressure pipes (a.k.a. force mains), valves, and stormwater conveyance systems within sewer system service area boundary, etc.

- Details for pipe diameters, and direction of flows be included on maps (a legend should be provided on maps for symbol clarity).

- If your agency is not the owner of the stormwater conveyance system, make every effort to obtain the maps, preferably in a format that is compatible with yours.

- Any format will do. If you are not able to obtain stormwater conveyance system maps, document your efforts to demonstrate your diligence.

UCSB maintains a comprehensive and up-to-date GIS that maps the locations of all sewer and stormwater conveyance infrastructure. The GIS database includes detailed spatial and attribute information for infrastructure assets owned and operated by UCSB across Main Campus, West Campus, Storke Campus, and North Campus, as well as pertinent assets managed by the GSD, GWSD, and the County of Santa Barbara. Sanitary sewer data within the GIS include attributes such as date of installation, pipe diameter, material type, designation as main or lateral, and identification as gravity or force mains. The system also captures the locations of associated features, including manholes, cleanouts, and pump stations, to support effective system management and planning.

## 4.2. Preventive Operation and Maintenance Activities

Regulatory Requirements - A scheduling system and a data collection system for preventive operation and maintenance activities conducted by staff and contractors. The scheduling system must include:

- Inspection and maintenance activities;

- Higher-frequency inspections;

- Maintenance of known problem areas including areas with tree root problems; and

- Regular visual and closed-circuit television (CCTV) inspections of manholes and sewer pipes.

The data collection system must document the data from system inspection and maintenance activities, including system areas/components prone to root-intrusion potentially resulting in system backup and/or failure.

Operation and maintenance of the sanitary sewer system is the primary responsibility of the FM and HDAE departments. This includes routine inspections and preventive maintenance of all main lines, manholes, and building lift and pump stations. FM is responsible for the operation and maintenance of laterals from academic, administrative, and support areas on campus. FM is also responsible for the operation and maintenance of building lift and pump stations (Table 4-1). HDAE is responsible for routine inspections and maintenance for all grease interceptors and traps and the operation and maintenance of laterals from residential and dining facilities.

FM and HDAE maintain separate computerized maintenance management systems (CMMS) to schedule and document all inspection and maintenance activities. These systems include information on the condition of sewer system components and identifies areas prone to root intrusion. Inspection and maintenance data, along with sanitary sewer spill history, are used to prioritize preventive work, plan future inspections, and support decisions regarding system repairs and capital improvements.

Routine Inspections:

- Pipelines: Periodic visual and closed-circuit television (CCTV) inspections are performed on pipelines over 8 inches in diameter. Visual inspections are performed more frequently on pipelines in known problem areas. Where feasible, 6-inch lines are also included in the inspection program.

- Manholes: Periodic inspections are conducted through system manholes, with priority given to high-demand and historically problematic areas. Over the course of the year, the majority of manholes are inspected at least once.

- Building Lift and Pump Stations: Real-time performance monitoring and system alerts are provided through the Metasys Building Automation System. Pump stations are visually inspected weekly. Except for KITP Scholars Residence, all building lift stations receive visual inspections at least once per month, with most checked more frequently. The KITP Scholars Residence lift station (Bldg. No. 834) is inspected annually.

- Grease Interceptors and Grease Traps: Contractors perform grease trap and interceptor inspections based on the frequencies outlined in Table 4-2.

- Emergency Standby Generators: Generator belly tanks are visually inspected monthly, quarterly and annual basis in accordance with the Steel Tank Institute (STI) Standard SP001 February 2024, 7th Edition.

Routine Maintenance:

- Pipelines: High-demand residential areas are cleaned biannually using hydro jetting equipment. Academic, administrative, and support areas are cleaned as needed, based on findings from inspections. Maintenance to address root intrusion is conducted as needed, based on findings from inspections.

- Manholes: Maintenance is performed as needed, based on findings from inspections.

- Building Lift and Pump Stations: Lift stations 529, 579, and 559 are equipped with odor control systems using natural filtration media (mushroom compost, wood chips, and water) to mitigate hydrogen sulfide gas and prevent system corrosion. Filter media beds are equipped with automated sprinkler systems. Wood chips and compost are replaced every four (4) years or as needed to mitigate odor.

- Grease Interceptors and Grease Traps: Contractors perform grease trap and interceptor cleanings based on the frequencies outlined in Table 4-2.

- Emergency Standby Generators: Generators are operated monthly under no-load conditions for 30 minutes to ensure readiness. Annual load testing is also performed, with additional time allocated for any needed repairs.

Table 4-1

UCSB Pump and Building Lift Stations

| Bldg. No. | Location | Type |
| --- | --- | --- |
| 529 | Main Gate Pump Station | Pump Station |
| 550 | Lagoon Pump House | Pump Station |
| 559 | North Pump Station | Pump Station |
| 579 | West Pump Station | Pump Station |
| 250 | Mesa Parking Structure | Building Lift Station |
| 220 | Electrical Shop | Building Lift Station |
| 251 | Psychology East | Building Lift Station |
| 505 | Events Center | Building Lift Station |
| 511 | Multi-Activity Center | Building Lift Station |
| 515 | Humanities and Social Science Building | Building Lift Station |
| 516 | Recreation Center | Building Lift Station |
| 531 | Music | Building Lift Station |
| 552 | Cheadle Hall | Building Lift Station |
| 555 | Marine Biotechnology Lab | Building Lift Station |
| 558 | University Center | Building Lift Station |
| 572 | Broida Hall | Building Lift Station |
| 583 | Aviary | Building Lift Station |
| 589 | Storke Tower | Building Lift Station |
| 834 | KITP Scholars Residence | Building Lift Station |
| 975 | Devereaux | Building Lift Station |
| 6850 | Portola | Building Lift Station |

Table 4-2

UCSB Grease Interceptors and Traps

| Bldg. No. | Location | Type | Size | Cleanout Frequency | Cleanout Vendor |
| --- | --- | --- | --- | --- | --- |
| 266 | Courtyard Cafe | Grease Interceptor | 1,000 gal | 2/ year | MarBorg |
| 501 | The Arbor | Grease Trap | 40 gal | 1/ month | MarBorg |
| 501 | Subway | Grease Trap | 40 gal | 1/ month | Marborg |
| 532 | Coral Tree Cafe | Grease Trap | 40 gal | 1/ month | MarBorg |
| 558 | UCen Central Kitchen | Grease Interceptor | 8,000 gal | 4/ year | MarBorg |
| 542 | Ortega Dining Commons | Grease Interceptor | 8,000 gal | 4/ year | MarBorg |
| 549 | De La Guerra Dining Commons | Grease Interceptor | 8,000 gal | 4/ year | MarBorg |
| 562 | Carrillo Dining Commons | Grease Interceptor | 1,500 gal | 4/ year | MarBorg |
| 580 | Harder Stadium | Grease Interceptor | 500 gal | 4/ year | MarBorg |
| 581 | Faculty Club | Grease Interceptor | 1,500 gal | 2/ year | MarBorg |
| 6850 | Portola Dining Commons | Grease Interceptor | 3,000 gal | 4/ year | MarBorg |

## 4.3. Training

Regulatory Requirement - In-house and external training provided on a regular basis for sanitary sewer system operations and maintenance staff and contractors.

The training must cover the requirements of this General Order; the Enrollee’s Spill Emergency Response Plan procedures and practice drills, skilled estimation of spill volume for field operators, and electronic CIWQS reporting procedures for staff submitting data.

Initial and annual training is conducted for employees that are responsible for preforming duties related to the sanitary sewer system. Initial training is conducted in collaboration between EH&S and DKF Solutions Group. Initial training items include:

- Requirements of the General Order;

- UCSB’s SERP procedures and practice drills;

- Skilled estimation of spill volume for field operators; and

- Electronic CIWQS reporting procedures for staff submitting data (for EH&S staff responsible for electronic reporting only).

Upon completion of initial training, employees are required annually to attend a live online training. Training records are maintained in a local electronic file system.

Additionally, UCSB utilizes a service agreement contract for outside contractors to perform maintenance on the sewer system. The service agreement contract stipulates that contractor’s staff must be properly trained.

## 4.4. Equipment Inventory

Regulatory Requirements - An inventory of sewer system equipment, including the identification of critical replacement and spare parts.

FM maintains a stockroom of essential replacement parts and emergency response equipment to support routine maintenance and immediate response needs. Emergency response equipment includes, but is not limited to: hydro jetting equipment, water pump, and portable lighting and generators. For larger and specialized repairs, UCSB relies on service agreements with qualified contractors who maintain inventories of critical components and are available for rapid deployment.

# 5. Design and Performance Provisions

The University has adopted the GSD design and performance standards, which are documented in the 2008 edition of GSD Standard Specifications for Design & Construction of Sanitary Sewers (GSD, 2008). Specifically, the University adopted Section 7 (Design Criteria), Section 9 (Construction Materials), Section 10 (Open Trench Construction Methods), Section 11 (Inspection and Testing), and Section 12 (Manhole Rehabilitation).

DCS, HDAE, and FM are responsible for ensuring that design and performance standards are implemented on campus.

## 5.1. Updated Design Criteria and Construction Standards and Specifications

Regulatory Requirements - The Plan must include the following items as appropriate and applicable to the Enrollee’s system. Updated design criteria, and construction standards and specifications, for the construction, installation, repair, and rehabilitation of existing and proposed system infrastructure components, including but not limited to pipelines, pump stations, and other system appurtenances. If existing design criteria and construction standards are deficient to address the necessary component-specific hydraulic capacity as specified in section 8 (System Evaluation, Capacity Assurance and Capital Improvements) of this Attachment, the procedures must include component-specific evaluation of the design criteria.

The GSD Standards establish design and construction requirements for new sewer systems, pump stations, and related infrastructure, as well as for the rehabilitation and repair of existing systems. These standards include detailed criteria for pipe materials, minimum pipe sizes and slopes, cover depth, structural strength, trenching and backfill procedures, and other essential specifications. All sanitary sewer construction, repairs, and rehabilitation projects must comply with the GSD Standards.

## 5.2. Procedures and Standards

Regulatory Requirements - Procedures, and standards for the inspection and testing of newly constructed, newly installed, repaired, and rehabilitated system pipelines, pumps, and other equipment and appurtenances.

Inspection and testing requirements for new and rehabilitated sewer infrastructure are defined in Section 11 (Inspection and Testing) of the GSD Standard Specifications for the Design and Construction of Sanitary Sewers (GSD, 2008). These procedures ensure that construction and rehabilitation work meet established standards. Acceptance testing for gravity sewers may include low-pressure air or water testing for leaks, mandrel testing for pipe deflection, vacuum or water testing of manholes, and CCTV inspection to detect grade deviations or construction defects. UCSB follows all inspection and testing protocols outlined in the GSD Standards for any new or rehabilitated sewer facilities.

# 6. Spill Emergency Response Plan

Regulatory Requirements - The Plan must include an up-to-date Spill Emergency Response Plan to ensure prompt detection and response to spills to reduce spill volumes and collect information for prevention of future spills. The Spill Emergency Response Plan must include procedures to meet all the following.

- Notify primary responders, appropriate local officials, and appropriate regulatory agencies of a spill in a timely manner.

- Notify other potentially affected entities (for example, health agencies, water suppliers, etc.) of spills that potentially affect public health or reach waters of the State.

- Comply with the notification, monitoring and reporting requirements of this General Order, State law and regulations, and applicable Regional Water Board Orders.

- Ensure that appropriate staff and contractors implement the Spill Emergency Response Plan and are appropriately trained.

- Address emergency system operations, traffic control and other necessary response activities.

- Contain a spill and prevent/minimize discharge to waters of the State or any drainage conveyance system.

- Minimize and remediate public health impacts and adverse impacts on beneficial uses of waters of the State.

- Remove sewage from the drainage conveyance system.

- Clean the spill area and drainage conveyance system in a manner that does not inadvertently impact beneficial uses in the receiving waters.

- Implement technologies, practices, equipment, and interagency coordination to expedite spill containment and recovery.

- Implement pre-planned coordination and collaboration with storm drain agencies and other utility agencies/departments prior, during, and after a spill event.

- Conduct post-spill assessments of spill response activities.

- Document and report spill events as required in this General Order.

- Annually, review and assess effectiveness of the Spill Emergency Response Plan, and update the Plan as needed.

Although the University takes proactive measures to prevent sanitary sewer overflows, spills may still occur. To ensure a safe, effective, and well-documented response, UCSB has developed a SERP, included in Appendix C.

# 7. Sewer Pipe Blockage Control Program

Regulatory Requirements - The Sewer System Management Plan must include procedures for the evaluation of the Enrollee’s service area to determine whether a sewer pipe blockage control program is needed to control fats, oils, grease, rags, and debris. If the Enrollee determines that a program is not needed, the Enrollee shall provide justification in its Plan for why a program is not needed. The procedures must include, at minimum:

- An implementation plan and schedule for a public education and outreach program that promotes proper disposal of pipe-blocking substances.

- A plan and schedule for the disposal of pipe-blocking substances generated within the sanitary sewer system service area. This may include a list of acceptable disposal facilities and/or additional facilities needed to adequately dispose of substances generated within a sanitary sewer system service area.

- The legal authority prohibits discharges to the system and identifies measures to prevent spills and blockages.

- Requirements to install grease removal devices (such as traps or interceptors), design standards for the removal devices, maintenance requirements, best management practices requirements, recordkeeping and reporting requirements.

- Authority to inspect grease producing facilities, enforcement authorities, and whether the Enrollee has sufficient staff to inspect and enforce the fats, oils, and grease ordinance.

- An identification of sanitary sewer system sections subject to fats, oils, and grease blockages and establishment of a cleaning schedule for each section; and

- Implementation of source control measures for all sources of fats, oils, and grease reaching the sanitary sewer system for each section identified above.

UCSB has determined that a sewer pipe blockage control program is necessary to prevent blockages in its sanitary sewer system caused by fats, oils, grease (FOG), rags, and debris. As part of this effort, UCSB regularly evaluates its sewer infrastructure and implements preventive measures to control the discharge and accumulation of pipe-blocking substances.

The campus sanitary sewer system includes several food service facilities equipped with grease traps or interceptors. These devices are located at dining commons, cafés, and other food service establishments and are designed to capture grease before it enters the sewer system. Grease removal devices are sized and installed in accordance with GSD specifications. All new food service construction or renovations involving grease-producing operations are required to include appropriate grease removal systems. Maintenance of these devices is performed either by campus staff or qualified contractors.

Preventive maintenance plays a critical role in UCSB’s blockage control efforts. Periodic inspections are conducted at key points in the collection system, including the University’s main lift station, to monitor for grease accumulation. When buildup is observed, staff take immediate steps to break down or remove the grease and notify GSD personnel if needed. FM coordinates with campus departments to investigate the source and address the issue to prevent further accumulation.

Proper handling and disposal of grease generated on campus is also essential to the effectiveness of the program. Kitchen staff are trained upon hiring in best management practices for grease handling and disposal. These practices include dry wiping pans, avoiding pouring grease down drains, and using sealed containers to collect and store excess grease. This grease is then removed from campus by licensed grease rendering companies on a regular schedule.

In addition to on-campus operations, the UCSB sanitary sewer system receives wastewater from Goleta Beach Park, which includes a restaurant. The restaurant is equipped with a 1,500-gallon grease interceptor that is inspected every 2 months. UCSB coordinates with the County of Santa Barbara and the GSD to ensure compliance with grease control requirements and to monitor for any potential contributions to blockages within the UCSB system.

# 8. System Evaluation, Capacity Assurance and Capital Improvements

Regulatory Requirements - The Plan must include procedures and activities for

- Routine evaluation and assessment of system conditions,

- Capacity assessment and design criteria.

- Prioritization of corrective actions.

- Capital improvement plan

## 8.1 System Evaluation and Condition Assessment

Regulatory Requirements - The Plan must include procedures to:

- Evaluate the sanitary sewer system assets utilizing the best practices and technologies available.

- Identify and justify the amount (percentage) of its system for its condition to be assessed each year.

- Prioritize the condition assessment of system areas that:

  - Hold a high level of environmental consequences if vulnerable to collapse, failure, blockage, capacity issues, or other system deficiencies.

  - Are located in or within the vicinity of surface waters, steep terrain, high groundwater elevations, and environmentally sensitive areas.

  - Are within the vicinity of a receiving water with a bacterial-related impairment on the most current Clean Water Act section 303(d) List (check with your local Regional Water Quality Control Board for their latest lists).

- Assess the system conditions using visual observations, video surveillance and/or other comparable system inspection methods.

- Utilize observations/evidence of system conditions that may contribute to exiting of sewage from the system which can reasonably be expected to discharge into a water of the State.

- Maintain documents and recordkeeping of system evaluation and condition assessment inspections and activities,

- Identify system assets vulnerable to direct and indirect impacts of climate change, including but not limited to sea level rise; flooding and/or erosion due to increased storm volumes, frequency, and/or intensity; wildfires; and increased power disruptions.

In 2004, UCSB launched a major infrastructure rehabilitation initiative that included addressing deficiencies in the campus sanitary sewer system. As part of this effort, a comprehensive assessment was conducted to evaluate system conditions and identify critical areas in need of improvement (Winzler and Kelly, 2004). The assessment focused on key concerns raised by UCSB staff, documented existing conditions using visual observations and video surveillance, and recommended necessary capital improvements.

The following deficiencies were identified:

- Several manholes were inaccessible or could not be located.

- The sewer system was bottlenecked in several areas, and some pipes were sloped counter to the direction of flow.

- Root intrusion was pervasive throughout the system.

- Grease traps were not present at food service areas.

- Flow metering devices were not installed.

- Although the network itself was structurally sound (minimal longitudinal cracking), many of the

manholes were in poor condition.

- A hydraulic model of the sanitary sewer system did not exist.

To address these deficiencies, UCSB implemented updates to its Operation and Maintenance Program and Sewer Pipe Blockage Control Program and launched a multi-phase capital improvement initiative focused on infrastructure renewal. Enhancements to the Operation and Maintenance Program included the installation of flow metering at the main lift station and the establishment of a routine inspection schedule for manholes and pipelines. Updates to the Sewer Pipe Blockage Control Program involved the installation of grease traps and interceptors at all food service facilities with the potential to discharge fats, oils, and grease (FOG) into the sanitary sewer system. As part of the first phase of the infrastructure renewal project, UCSB developed a hydraulic model of the sanitary sewer system to assess capacity and evaluate future campus buildout scenarios. Between 2014 and 2017, UCSB replaced or installed new sewer lines and manholes as needed to correct root intrusion and corrosion issues, eliminate bottlenecks, and accommodate projected increases in flow. Pipe sizes were determined based on the results of the hydraulic model.

As part of UCSB’s efforts to assess sanitary sewer system assets vulnerable to climate change, the University prepared a Sea Level Rise Adaptation Strategy (UCSB, 2024b). Finalized in June 2024, the strategy applies the best available science to evaluate the vulnerability of the campus’s built and natural environments to erosion, flooding, and other coastal hazards, assuming up to 2 meters (6.6 feet) of sea level rise by 2100 (SLR Plan, 2024). The SLR Plan concludes that most of UCSB’s built environment is located on an elevated marine terrace, relatively protected from coastal hazards. However, the campus still faces significant risks from shoreline erosion, flooding, and rising water tables. The area along Lagoon Road is among the most vulnerable to coastal hazards, where bluff erosion presents a significant risk to the roadway and critical underground infrastructure, including sanitary sewer lines. Adaptation strategies, developed using the best available science and consistent with state and university policy requirements, are further detailed in the SLR Plan.

## 8.2. Capacity Assessment and Design Criteria

Regulatory Requirements - The Plan must include procedures to identify system components that are experiencing or contributing to spills caused by hydraulic deficiency and/or limited capacity, including procedures to identify the appropriate hydraulic capacity of key system elements for:

- Dry-weather peak flow conditions that cause or contribute to spill events.

- The appropriate design storm(s) or wet weather events that causes or contributes to spill events.

- The capacity of key system components.

- Identify the major sources that contribute to the peak flows associated with sewer spills.

The capacity assessment must consider:

- Data from existing system condition assessments, system inspections, system audits, spill history, and other available information.

- Capacity of flood-prone systems subject to increased infiltration and inflow, under normal local and regional storm conditions.

- Capacity of systems subject to increased infiltration and inflow due to larger and/or higher intensity storm events as a result of climate change.

- Increases of erosive forces in canyons and streams near underground and aboveground system components due to larger and/or higher-intensity storm events.

- Capacity of major system elements to accommodate dry weather peak flow conditions, and updated design storm and wet weather events; and

- Necessary redundancy in pumping and storage capacities.

To evaluate hydraulic capacity and identify components of the sanitary sewer system vulnerable to spills due to hydraulic deficiencies or limited capacity, UCSB commissioned a comprehensive infrastructure assessment and hydraulic modeling effort (Penfield & Smith, 2008). As part of this effort, all accessible sewer manholes across UCSB’s main campus were surveyed, documented, and evaluated for structural condition. The survey included photographic documentation, condition assessments, and invert elevation measurements. Survey data and existing campus infrastructure records were used to evaluate the capacity of key system components under existing and projected future flow conditions.

Average, peak dry, and peak wet weather flows were estimated using wastewater flow data measured at the intake to the GSD Wastewater Treatment Plant. A peak dry weather flow of 596.5 gallons per minute (GPM), recorded in March 2006, was used to represent maximum dry weather conditions. The highest recorded wet weather flow was 764 GPM, measured during a 50-year storm event in January 1995, and was used to represent peak wet weather conditions. Future wastewater loading scenarios were estimated based on anticipated campus growth outlined in UCSB’s 2010 Long Range Development Plan (UCSB, 2010). For West and Storke Campuses, a multiplication factor of 3 was applied to existing flows to account for planned residential development. For the main campus, projected flow increases were allocated by building type and square footage using weighting factors derived from occupancy standards in the California Building Code. These projections allowed the model to estimate peak flows under future build-out conditions.

Modeling results confirmed that the existing sewer system possesses adequate hydraulic capacity to convey both current and future peak wet weather flows. However, the assessment also highlighted the need for ongoing condition monitoring and rehabilitation, as system performance could be compromised by structural defects such as root intrusion, corrosion, or accumulated debris. The hydraulic model and supporting infrastructure data continue to serve as a tool for UCSB’s capacity assessment, operation and maintenance planning, and capital improvement efforts.

## 8.3. Prioritization of Corrective Action

Regulatory Requirements - The findings of the condition assessments and capacity assessments must be used to prioritize corrective actions. Prioritization must consider the severity of the consequences of potential spills.

UCSB uses the findings from condition and capacity assessments to prioritize corrective actions based on the severity and potential consequences of sanitary sewer overflows. CCTV inspections, manhole condition reports, lift station evaluations, and hydraulic model updates are evaluated to determine risk and urgency. All inspection records and system evaluation documentation are maintained to support ongoing prioritization and planning efforts.

## 8.4. Capital Improvement Plan

Regulatory Requirements - The capital improvement plan must include the following items:

- Project schedules include completion dates for all portions of the capital improvement program.

- Internal and external project funding sources for each project.

- Joint coordination between operation and maintenance staff, and engineering staff/consultants during planning, design, and construction of capital improvement projects; and Interagency coordination with other impacted utility agencies.

UCSB undertakes capital improvement projects as needed to maintain the integrity and performance of the sanitary sewer system. These efforts are guided by system assessments, operational needs, and long-term campus planning considerations. Project management is typically led by DCS staff, with substantial input from engineering and construction consultants. Operations and maintenance staff – including FM, HDAE, and EH&S – provide input throughout the planning, design, and construction phases. Where applicable, coordination with outside utility agencies is incorporated. Funding sources vary depending on project scope and available resources.

| Type of Project | Capital Improvement Plan |
| --- | --- |
| Completed Projects | Infrastructure Renewal Project: UCSB completed all phases of the Infrastructure Renewal Project in 2017. As part of this project, targeted pipeline and manhole replacement and rehabilitation were performed to improve sanitary sewer system performance and reduce the risk of overflows. |
| Short-Term Projects (0-10 years) | A condition assessment of Pump Station 559 was completed by Phoenix Civil Engineering on April 28, 2025. The final report was issued on November 17, 2025. To address identified deficiencies, $730,800 in campus deferred maintenance funding has been approved for the following improvements: - Influent and wet well rehabilitation - Transformer pad replacement - Piping replacement from pumps to force main - Pump replacements - Check valve replacements - VFD replacements Project completion is anticipated by the end of calendar year 2026. |
| Mid-Term Projects (10-30 years) | To be determined. No mid-term capital sewer projects have been identified at this time. UCSB will update this section as future system assessments and campus development plans identify needs within this timeframe. |
| Long-Term Projects (30-80 years) | Lagoon Road Utility Realignment: As detailed in the SLR Plan, bluff erosion along Lagoon Road may necessitate future realignment of sewer and other utility infrastructure. Ongoing erosion monitoring and future site assessments will inform the development of a shoreline management plan that considers both managed retreat and alternative adaption strategies such as bluff armoring. |

# 9. Monitoring, Measurement and Program Modifications

Regulatory Requirements - The Plan must include an Adaptive Management section that addresses Plan-implementation effectiveness and the steps for necessary Plan improvement, including:

- Maintaining relevant information, including audit findings, to establish and prioritize appropriate Plan activities.

- Monitoring the implementation and measuring the effectiveness of each Plan Element.

- Assessing the success of the preventive operation and maintenance activities.

- Updating Plan procedures and activities, as appropriate, based on results of monitoring and performance evaluations; and

- Identifying and illustrating spill trends, including spill frequency, locations, and estimated volumes.

Key personnel from EH&S, FM, HDAE, and DCS are responsible for monitoring the implementation and effectiveness of this Plan and updating this Plan as required and needed (Table 2-1). Every three years, members from each department will conduct a comprehensive review of each element of this Plan. Program elements are updated based on monitoring or performance evaluation. This Plan is available for audit at all times.

# 10. Internal Audits

Regulatory Requirements - The Plan shall include internal audit procedures, appropriate to the size and performance of the system, for the Enrollee to comply with section 5.4 (Sewer System Management Plan Audits) of this General Order.

In accordance with Section 5.4 of the General Order, UCSB conducts periodic internal audits of this Plan at least once every three years. Each audit covers the period following the end of the previous audit cycle and includes consideration of the number and nature of sanitary sewer overflows (SSOs) in that timeframe. The SSMP Audit is used to assist in evaluating each element of the Plan. This review helps to identify any deficiencies and inform recommendations for corrective actions.

The audit report, including findings, recommended corrective actions, and a statement of operator input, is submitted by the LRO to the CIWIQS Sanitary Sewer System Database within six months of the end of the audit period.

# 11. Communication Program

Regulatory Requirements - The Plan must include procedures for the Enrollee to communicate with:

- The public for spills and discharges resulting in closures of public areas, or that enter a source of drinking water, and the development, implementation, update of its Plan, including opportunities for public input to Plan implementation and updates.

- Owners/operators of systems that connect into the Enrollee’s system, including satellite systems, for system operation, maintenance, and capital improvement-related activities.

This Plan is updated regularly to reflect significant changes in proposed actions or implementation schedules. UCSB will communicate implementation and performance updates to interested parties, including:

- Associated Students Environmental Affairs;

- GSD; and

- GWSD.

The most current version of the Plan is available on the UCSB EH&S website for the campus community review and comment.

# 12. References

GSD, 2008. Goleta Sanitary District Standard Specification for Design & Construction of Sanitary Sewers. February 2008.

Penfield & Smith, 2008. UCSB Infrastructure Renewal Existing Conditions Assessment Phase 1 Summary Report. September 2008.

SWRCB, 2022. Order No. 2022-0103-DWQ: Statewide Sanitary Sewer Systems General Order. December 2022.

UCSB, 2010. Long Range Development Plan. July 2010.

UCSB, 2024a. 2023-24 Campus Profile. April 2024.

UCSB, 2024b. UCSB Sea Level Rise Adaptation Strategy. June 2024.

Winzler & Kelly, 2004. University of California, Santa Barbara Infrastructure Assessment Final Report. December 2004

Appendix A: UCSB Sanitary Sewer System Service Area Boundary

# UCSB Sanitary Sewer System Service Area Boundary

## Map Details:

- Scale: The map covers an area approximately 1.5 miles wide from west to east.

- Service Areas: The boundary is delineated by a thick, dashed black line encompassing five primary zones:

  - Main Campus: Located on the easternmost side of the boundary, bordered by the coastline to the south and east.

  - Storke Campus: Centrally located, north of the residential/urban grid.

  - North Campus: Situated in the northernmost section, adjacent to a green space and housing.

  - West Campus: The westernmost section, bordering the coastline to the south.

  - Other / Offsite: Identified by red-shaded regions to the north of the primary campus blocks.

- Contextual Landmarks: The Santa Barbara Airport runways are visible to the north of the service boundary.

Appendix B: Goleta Beach Park Spill Emergency Response Plan

# Goleta Beach Emergency Sewer Overflow Response Plan

## Responding, Containing, and Cleaning Up Sewage Overflows

### Responding

A High-Level Alarm System is installed in the lift station. Staff needs to be notified their response time can be within 10 minutes during work hours. After hours, if Goleta Beach Rangers are not able to respond, a call out could take 20 to 30 minutes.

### When a sewage spill/overflow occurs, the first people to be notified are the Goleta Beach Park Ranges, plumber and UCSB 24 Hr. Phone Number (805) 893-3000

Brian Switzer 	Work: (805) 967-1300

Cell: (805) 896-1036

Mark Hopson	Work: (805) 967-1300

Cell: (805) 896-70823

### If Resident rangers are not in the park, contact:

Deputy Park Director, Jeffrey Lindgren	Work: (805) 681-5651

Cell: (805) 686-5076

Park Operations Manager, Lloyd Henning	Work: (805) 681-5653

Cell: (805) 729-7507

Maintenance Leader, Mario Reynoso	Work: (805) 681-5656

Cell: (805) 896-1553

Maintenance Plumber	Work: (805) 681-5656

### Response Contact Agencies:

Marborg Disposal	24 Hr.: (805) 963-1852

Cell: (805) 896-8047

RJ Carroll and Sons	24 Hr.: (805) 963-8711

Goleta Sanitary District	24 Hr.: (805) 967-4519

UCSB	24 Hr.: (805) 893-3000

Appendix C: UCSB Spill Emergency Response Plan

UCSB Spill Emergency Response Plan is available on our website or as requested.